Caledonian Mining Cables

Cables for Open-cast Mining

NTMCWOEU Flexible Medium Voltage Single Core Cable

�  Applications

These cables are used for connection in switch-gear and for connection of mobile transformer substations to the overhead line.

�  Standards

VDE 0250 Part 813

�  Construction

Stranded Tinned Copper Conductor 3GI3 Rubber Insulation

Copper Wire Screen

5GM3 Rubber Outer Sheath

Conductors: Flexible stranded tinned copper conductor, class 5 according to DIN VDE 0295.

Inner Conductor Layer: Special conductive rubber.

Insulation: EPR type 3GI3.

Outer Conductor Layer: Special conductive rubber.

Screen: Spiral of tinned copper wires.

Outer Sheath: PCP type 5GM3.

�  Dimensions and Weight

6/10kV

| Number of Cores譔ominal Cross Section | Insulation Thickness | Thickness of Outer Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- |
| No. 譵m� | mm | mm | mm | kg/km |
| 1�16/16 | 3�4 | 2�2 | 22�0 | 760 |
| 1�25/16 | 3�4 | 2�2 | 23�5 | 910 |

68	www.caledonian-cables.co.uk  www.addison-cables.com

Caledonian Mining Cables Cables for Open-cast Mining

| Number of Cores譔ominal Cross Section | Insulation Thickness | Thickness of Outer Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- |
| No. 譵m� | mm | mm | mm | kg/km |
| 1�35/16 | 3�4 | 2�2 | 24�5 | 1040 |
| 1�50/16 | 3�4 | 2�2 | 27�0 | 1260 |
| 1�70/16 | 3�4 | 2�5 | 28�5 | 1530 |
| 1�95/16 | 3�4 | 2�5 | 30�5 | 1770 |
| 1�120/16 | 3�4 | 2�5 | 33�5 | 2180 |
| 1�150/25 | 3�4 | 3�0 | 35�0 | 2550 |
| 1�185/25 | 3�4 | 3�0 | 37�0 | 2900 |
| 1�240/25 | 3�4 | 3�5 | 41�0 | 3590 |
| 1�300/25 | 3�4 | 3�5 | 43�0 | 4280 |
| 1�400/35 | 3�4 | 4�0 | 46�0 | 5120 |
| 1�500/35 | 3�4 | 4�0 | 49�0 | 5950 |
| 1�630/35 | 3�4 | 4�0 | 53�5 | 7860 |

12/20kV

| Number of Cores譔ominal Cross Section | Insulation Thickness | Thickness of Outer Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- |
| No. 譵m� | mm | mm | mm | kg/km |
| 1�25/16 | 5�5 | 2�5 | 28�0 | 1180 |
| 1�35/16 | 5�5 | 2�5 | 29�5 | 1320 |
| 1�50/16 | 5�5 | 2�5 | 31�5 | 1560 |
| 1�70/16 | 5�5 | 3�0 | 34�0 | 1920 |
| 1�95/16 | 5�5 | 3�0 | 36�0 | 2190 |
| 1�120/16 | 5�5 | 3�0 | 38�0 | 2460 |
| 1�150/25 | 5�5 | 3�5 | 40�0 | 2990 |
| 1�185/25 | 5�5 | 3�5 | 42�0 | 3350 |
| 1�240/25 | 5�5 | 3�5 | 45�0 | 3990 |
| 1�300/25 | 5�5 | 3�5 | 48�0 | 4760 |
| 1�400/35 | 5�5 | 4�0 | 52�0 | 6100 |
| 1�500/35 | 5�5 | 4�0 | 56�0 | 7010 |
| 1�630/35 | 5�5 | 4�0 | 60�0 | 8180 |

14/25kV

| Number of Cores譔ominal Cross Section | Insulation Thickness | Thickness of Outer Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- |
| No. 譵m� | mm | mm | mm | kg/km |
| 1�25/16 | 6�8 | 3�0 | 30�5 | 1300 |
| 1�300/25 | 6�8 | 4�0 | 49�0 | 4900 |

www.caledonian-cables.co.uk  www.addison-cables.com	69

Caledonian Mining Cables

Cables for Open-cast Mining

18/30kV

| Number of Cores譔ominal Cross Section | Insulation Thickness | Thickness of Outer Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- |
| No. 譵m� | mm | mm | mm | kg/km |
| 1�50/16 | 8�0 | 3�0 | 35�0 | 1870 |

20/35 kV

| Number of Cores譔ominal Cross Section | Insulation Thickness | Thickness of Outer Sheath | Nominal Overall Diameter | Nominal Weight |
| --- | --- | --- | --- | --- |
| No. 譵m� | mm | mm | mm | kg/km |
| 1�95/16 | 9�5 | 3�5 | 44�0 | 2900 |
| 1�150/25 | 9�5 | 3�5 | 46�3 | 3600 |
| 1�240/25 | 9�5 | 4�0 | 51�7 | 5000 |

70	www.caledonian-cables.co.uk  www.addison-cables.com